## Fault Taxonomy
D-NAVIO — Fault Taxonomy
FM ID | FM Class | Failure Mode (FM) | Potential Cause(s) & Mechanism(s) | Potential Technical Effects on the Asset | Potential Consequences | Severity (1-10) | Probability (1-10) | Detective Controls | Preventive Controls | Responsibility | Source | Link | Column Guide
[13 empty] | Column | Description
D-NAVIO — Fault Taxonomy | [12 empty] | FM ID | Distinct Failure Mode ID in the form "Asset initials - XX" (e.g. PMP-01).
FM ID | FM Class | Failure Mode (FM) | Potential Cause(s) & Mechanism(s) | Potential Technical Effects on the Asset | Potential Consequences | Severity (1-10) | Probability (1-10) | Detective Controls | Preventive Controls | Responsibility | Source | Link | FM Class | Group or classification for the asset's failure mode.
GEN-01 | Electrical System | Phase Imbalance | Stator winding failure, defective cable termination | Unequal phase currents cause excessive heating in stator windings and rotor components. Reduced generator efficiency and accelerated insulation ageing may occur. | Reduced power quality, nuisance protection trips, load shedding and possible generator outage | 8 | 4 | Power quality monitoring, phase current trending, protective relay alarms, thermography. | Periodic connection inspections, load balancing, insulation testing. | Electrical Engineer, Chief Engineer | ABB. Motor and Generator Preventive Maintenance. Document No: 9AKK108466A1295. ABB Electrification Service. Revision A. Sections L1-L4 Maintenance Programme. | https://search.abb.com/library/Download.aspx?DocumentID=9AKK108466A1295 | Failure Mode (FM) | Concise & comprehensive name for the failure mode.
GEN-02 | Electrical System | Insulation Failure | Moisture ingress, aging, contamination | Breakdown of winding insulation can cause leakage current, partial discharge, winding overheating and short circuits. | Generator trip, fire risk, loss of electrical supply to essential services, possible blackout. | 10 | 5 | Insulation resistance testing, polarization index testing, partial discharge monitoring, thermal monitoring. | Moisture control, scheduled insulation testing, cleaning, drying procedures, preventive rewinds when required. | Electrical Engineer, Service Engineer | ABB, Motor and Generator Preventive Maintenance, Document No. 9AKK108466A1295, Electrification Service, Recommended Maintenance Program, Sections L1-L4. | https://search.abb.com/library/Download.aspx?DocumentID=9AKK108466A1295 | Potential Causes | Brief description of the FM's causes, and the mechanism(s) which lead to the FM. 2-3 concise sentences.
GEN-03 | Rotor Assembly | Unstable Frequency | Governor failure, incrorrect load sharing | Generator speed variations cause frequency fluctuations and poor electrical output quality. Sensitive equipment may malfunction. | Synchronization problems, performance degradation. | 7 | 4 | Frequency monitoring, governor diagnostics, alarm logs, power management system data. | Governor maintenance, calibration, load-sharing verification, routine testing. | Electrical Engineer, Chief Engineer | ABB. Motor and Generator Preventive Maintenance. Document No: 9AKK108466A1295. ABB Electrification Service. Revision A. Sections L1-L4 Maintenance Programme. | https://search.abb.com/library/Download.aspx?DocumentID=9AKK108466A1295 | Potential Technical Effects | Brief description of the FM's effects on the asset. 2-3 concise sentences.
GEN-04 | Stator Assembly | Overheating | Failure in cooling water system, bearing failure | Excessive temperature accelerates insulation degradation, bearing wear and winding damage. Generator efficiency decreases. | Generator protective trip may result in loss of available electrical generation capacity. If operating redundancy is insufficient, the event may contribute to blackout condition | 9 | 5 | Temperature sensors, thermal imaging, vibration monitoring, cooling-system alarms. | Cooling system maintenance, evaluation of lubrication | Electrical Engineer, Chief Engineer | ABB, Motor and Generator Preventive Maintenance, Document No. 9AKK108466A1295, Electrification Service, Recommended Maintenance Program, Sections L1-L4. | https://search.abb.com/library/Download.aspx?DocumentID=9AKK108466A1295 | Potential Consequences | Brief description of the FM's consequences. These are the results (consequences) most important for the entire ships' high level operations. 2-3 concise sentences. It is ok if there is some overlapping with the Pot. Technical Effects.
GEN-05 | Stator Assembly | Stator Winding Failure | Excessive thermal stress, vibration, insulation breakdown | Shorted or open turns develop within stator windings, causing local heating and loss of generating capability. | Generator shutdown, significant power loss, possible emergency generator operation. | 10 | 4 | Differential protection, insulation testing, winding temperature monitoring, partial discharge analysis. | Thermal load management, insulation maintenance, vibration control, periodic testing. | Electrical Engineer, OEM Service Engineer | ABB. Motor and Generator Preventive Maintenance. Document No: 9AKK108466A1295. ABB Electrification Service. Revision A. Sections L1-L4 Maintenance Programme. | https://search.abb.com/library/Download.aspx?DocumentID=9AKK108466A1295 | Severity (1-10) | Severity score of the FM (1-10). (optional)
GEN-06 | Cooling System | Overheating | Lack of fresh water cooling capacity, incorrect 3way control valve setting, incorrect cooling water setting | localised hot spots causing progressive degradation of generator components | Loss of generating capability may reduce electrical power redundancy and increase blackout risk. | 10 | 4 | Core flux testing, thermal inspections, vibration analysis, electrical testing. | Proper maintenance practices, overload avoidance, cooling system upkeep. | OEM Service Engineer, Electrical Engineer | ABB, Motor and Generator Preventive Maintenance, Document No. 9AKK108466A1295, Electrification Service, Recommended Maintenance Program, Sections L1-L4. | https://search.abb.com/library/Download.aspx?DocumentID=9AKK108466A1295 | Probability (1-10) | Probability score of the FM (1-10). (optional)
GEN-07 | Rotor Assembly | Rotor Imbalance | Incorrect installation, bearing wear, engine-generator coupling fault | Increased vibration loads bearings and coupling components, resulting in fatigue damage and reduced machine life. | Excessive vibration may force generator shutdown and reduce power generation capacity. Loss of redundancy increases the likelihood of load shedding and blackout events. | 10 | 4 | Vibration analysis, shaft orbit monitoring, bearing temperature trends. | Correct installation, balancing, alignment verification and periodic vibration surveys. | Chief Engineer, Service Engineer | ABB. Motor and Generator Preventive Maintenance. Document No: 9AKK108466A1295. ABB Electrification Service. Revision A. Sections L1-L4 Maintenance Programme. | https://search.abb.com/library/Download.aspx?DocumentID=9AKK108466A1295 | Detective Controls | How the FM can be detected. (optional)
GEN-08 | Electrical Connections | Slip Ring Wear | Sustained overload, mist or salt contamination | Increased contact resistance causes unstable excitation current, sparking and heat generation. | Loss of voltage control, generator instability and possible unit trip. | 7 | 5 | Visual inspection, brush wear measurements, excitation current monitoring. | Regular cleaning, brush replacement, contamination control and scheduled maintenance. | Electrical Engineer | ABB, Motor and Generator Preventive Maintenance, Document No. 9AKK108466A1295, Electrification Service, Recommended Maintenance Program, Sections L1-L4. | https://search.abb.com/library/Download.aspx?DocumentID=9AKK108466A1295 | Preventive Controls | How the FM can be prevented. (optional)
GEN-09 | Bearing | Bearing Failure | Lubrication failure, electrical discharge | Excessive friction, vibration and heat lead to shaft support degradation and eventual seizure. Bearing failures are commonly detected by monitoring vibration, temperature and lubrication condition. | Generator trip, collateral rotor/stator damage, extended downtime and potential blackout risk if redundancy is limited. | 9 | 6 | Vibration monitoring, temperature trending, lubrication analysis, acoustic monitoring. | Correct lubrication, contamination control, alignment checks and condition-based maintenance. | Electrical Engineer | SKF, Bearing Damage and Failure Analysis, Publication 457725, Rev. 2018, Chapter 2 Inspection and Troubleshooting, pp. 8-10; Chapter 4 Failure Modes Classification, pp. 42-59. | https://cdn.skfmediahub.skf.com/api/public/093168a92d25cc46/pdf_preview_medium/093168a92d25cc46_pdf_preview_medium.pdf | Responsibility | Who is responsible for addressing the FM. (optional)
GEN-10 | Circuit Breaker System | Loose Terminals | Vibration | High contact resistance creates localized heating, arcing and voltage instability. | Fire risk, protection trips, equipment damage and interruption of power supply. | 7 | 5 | Infrared thermography, visual inspection, voltage drop measurements. | Torque inspections, vibration checks and electrical maintenance procedures. | Electrical Engineer | Schneider Electric. FlexSet Switchboards Instruction Bulletin. Document No. JYT1078000. Section: Maintaining the Switchboard. Recommended annual inspection programme. | https://productinfo.se.com/jyt1078000_flexset_switchboards_ib/ | Source | Reference in the form of a scientific paper citation.
GEN-11 | Power Distribution System | Cable Insulation Breakdown | Moisture ingress, excessive bending stress | Electrical leakage, short circuiting and flashover may occur between conductors or to ground. | Generator trip, fire hazard and loss of critical electrical distribution. | 9 | 4 | Insulation resistance testing, cable condition inspection, protection relay alarms. | Proper cable routing, moisture protection, routine insulation testing and replacement of degraded cables. | Electrical Engineer, Electrical Technician | ABB. Motor and Generator Preventive Maintenance. Document No: 9AKK108466A1295. ABB Electrification Service. Revision A. Sections L1-L4 Maintenance Programme. | https://search.abb.com/library/Download.aspx?DocumentID=9AKK108466A1295 | Link | URL of the source.
GEN-12 | Excitation System | AVR Failure | Electronic component failure, sensing faults or power supply issues impair voltage regulation. Excitation control is lost or degraded. | Overvoltage, undervoltage or unstable terminal voltage occurs. Generator may trip on protection. | Power quality issues can disrupt propulsion drives, automation systems and parallel operation. | 8 | 4 | Voltage trending; AVR diagnostics; alarm monitoring | Periodic AVR testing and calibration | Electrical Engineer | ABB UNITROL 1000 AVR Product Information | https://www.abb.com/global/en/areas/power-conversion-control/excitation-systems/unitrol-excitation-systems/unitrol-1000
GEN-13 | Excitation System | Excitation System Failure | Failure of exciter windings, rotating diodes or excitation circuitry prevents adequate field current. Generator cannot sustain voltage. | Output voltage collapses or cannot build up under load. Generator becomes unavailable. | Immediate reduction in power generation can lead to blackout if loading is high. | 9 | 4 | Excitation current monitoring; diode testing | Scheduled exciter inspections | Electrical Engineer | ABB excitation systems technical information, 2025 | https://library.abb.com/share?cid=9AAC166046