## Fault Taxonomy
D-NAVIO — Fault Taxonomy
FM ID | FM Class | Failure Mode (FM) | Potential Cause(s) & Mechanism(s) | Potential Technical Effects on the Asset | Potential Consequences | Severity (1-10) | Probability (1-10) | Detective Controls | Preventive Controls | Responsibility | Source | Link | Column Guide
[13 empty] | Column | Description
D-NAVIO — Fault Taxonomy | [12 empty] | FM ID | Distinct Failure Mode ID in the form "Asset initials - XX" (e.g. PMP-01).
FM ID | FM Class | Failure Mode (FM) | Potential Cause(s) & Mechanism(s) | Potential Technical Effects on the Asset | Potential Consequences | Severity (1-10) | Probability (1-10) | Detective Controls | Preventive Controls | Responsibility | Source | Link | FM Class | Group or classification for the asset's failure mode.
SWB-01 | Busbar | Busbar overheating | Busbar misalignment, loose connections, corrosion and moisture ingress increase contact resistance. Elevated resistance causes localised heating and progressive deterioration of conductors and insulation. | Excessive temperatures degrade insulation, distort busbars and reduce current carrying capacity. Prolonged overheating can damage adjacent switchgear and protective devices. | Protection trips, loss of power distribution may occur. Essential services, propulsionand cargo operations can be disrupted and blackout risk increases. | 9 | 5 | Infrared thermography; temperature monitoring; visual inspection; current trending; switchboard alarms | Routine checks; cleaning; corrosion control; thermographic inspections; load balancing | Electrical Engineer; Chief Engineer | Schneider Electric. FlexSet Switchboards Instruction Bulletin. Document No. JYT1078000. Section: Maintaining the Switchboard. Periodic inspection, busbar maintenance, breaker testing and maintenance requirements. | https://productinfo.se.com/jyt1078000_flexset_switchboards_ib/ | Failure Mode (FM) | Concise & comprehensive name for the failure mode.
SWB-02 | Busbar | Busbar Insulation failure | Moisture ingress, contamination, ageing and maintenance damage reduce dielectric strength. Partial discharge eventually lead to insulation breakdown. | Phase-to-phase or phase-to-ground faults may develop. Severe internal arcing can damage switchboard and associated equipment. | Major electrical faults can result in fire, equipment damage and vessel blackout. Navigation, propulsion and safety systems may be adversely affected. | 10 | 4 | Insulation resistance testing; partial discharge monitoring; thermography; visual inspection; relay alarms | Environmental control; insulation testing; cleaning programmes; replacement of degraded insulation materials | Electrical Engineer; Electrical technician | Schneider Electric. FlexSet Switchboards Instruction Bulletin. Document No. JYT1078000. Section: Maintaining the Switchboard. Periodic inspection, busbar maintenance, breaker testing and maintenance requirements. | https://productinfo.se.com/jyt1078000_flexset_switchboards_ib/ | Potential Causes | Brief description of the FM's causes, and the mechanism(s) which lead to the FM. 2-3 concise sentences.
SWB-03 | Circuit Breaker System | Breaker (fail to close) | Mechanical wear, damaged operating mechanisms, defective closing coils or interlock faults prevent breaker closure. Loss of control power may also inhibit operation. | Generators and consumers cannot be connected when required. Available system redundancy is reduced. | Loss of standby generationavailability compromise operational resilience during failure conditions. | 7 | 4 | Breaker functional testing; status indication monitoring; control circuit diagnostics; alarm review | Scheduled breaker maintenance; lubrication; testing of closing circuits; OEM overhaul intervals | Electrical Engineer; Service Engineer | Schneider Electric. FlexSet Switchboards Instruction Bulletin. Document No. JYT1078000. Section: Maintaining the Switchboard. Periodic inspection, busbar maintenance, breaker testing and maintenance requirements. | https://productinfo.se.com/jyt1078000_flexset_switchboards_ib/ | Potential Technical Effects | Brief description of the FM's effects on the asset. 2-3 concise sentences.
SWB-04 | Circuit Breaker System | Breaker (fail to open) | Mechanical seizure, trip coil failure or defective protection circuits prevent breaker interruption. Fault current continues flowing into the affected circuit. | Safe fault isolation is lost and fault energy remains connected. Adjacent equipment may suffer secondary damage. | Arc flash, fire and cascading electrical failures may occur. Personnel safety and vessel electrical stability are significantly threatened. | 10 | 3 | Trip testing; protection relay testing; event recorder analysis; breaker inspections | Periodic trip verification; protective relay maintenance; preventive component replacement | Electrical Engineer | Schneider Electric. FlexSet Switchboards Instruction Bulletin. Document No. JYT1078000. Section: Maintaining the Switchboard. Periodic inspection, busbar maintenance, breaker testing and maintenance requirements. | https://productinfo.se.com/jyt1078000_flexset_switchboards_ib/ | Potential Consequences | Brief description of the FM's consequences. These are the results (consequences) most important for the entire ships' high level operations. 2-3 concise sentences. It is ok if there is some overlapping with the Pot. Technical Effects.
SWB-05 | Protection System | Tripping | Incorrect protection settings, electrical transients, harmonics or grounding deficiencies cause unwanted breaker operations. Healthy circuits are disconnected unnecessarily. | Electrical feeders are interrupted despite absence of true faults. Repeated tripping accelerates breaker wear. | Critical consumers may be lost unexpectedly causing operational disruption, reduced reliability and possible propulsion support issues. | 7 | 6 | Event log review; relay diagnostics; power quality monitoring; alarm trending | Protection coordination studies; relay calibration; harmonic mitigation; grounding inspections | Electrical Engineer; Chief Engineer | Schneider Electric. FlexSet Switchboards Instruction Bulletin. Document No. JYT1078000. Section: Maintaining the Switchboard. Periodic inspection, busbar maintenance, breaker testing and maintenance requirements. | https://productinfo.se.com/jyt1078000_flexset-switchboards_ib/ | Severity (1-10) | Severity score of the FM (1-10). (optional)
SWB-06 | Contactor | Contact wear/erosion | Frequent switching operations and arcing progressively remove contact material. Increased resistance develops across the contact surfaces. | Overheating, voltage drops and unreliable switching performance occur. Advanced wear may lead to contact welding or failure. | Distribution reliability is reduced and the likelihood of feeder outages increases. Equipment availability and vessel operations may be affected. | 7 | 6 | Thermography; contact resistance testing; visual inspection; breaker maintenance records | Periodic overhaul; contact replacement; adherence to OEM maintenance schedules | Electrical Engineer; Technician | Schneider Electric. FlexSet Switchboards Instruction Bulletin. Document No. JYT1078000. Section: Maintaining the Switchboard. Periodic inspection, busbar maintenance, breaker testing and maintenance requirements. | https://productinfo.se.com/jyt1078000_flexset_switchboards_ib/ | Probability (1-10) | Probability score of the FM (1-10). (optional)
SWB-07 | Synchronisation | Synchronising failure | Voltage, frequency or phase angle mismatch caused by faulty instrumentation, control system errors or unstable generators prevents successful synchronization. Incoming generators cannot be safely paralleled. | Generator connection attempts fail and synchronization alarms are generated. Electrical stress may occur if incorrect synchronization is attempted. | Loss of generating redundancy increases blackout risk and can affect propulsion and essential services | 8 | 4 | Synchronizing relay checks; PMS alarms; voltage monitoring; frequency monitoring; operator observation | Calibration of synchronizing equipment; AVR maintenance; governor testing; routine synchronization drills | Electrical Engineer; Chief Engineer | ABB. Motor and Generator Preventive Maintenance. Document No. 9AKK108466A1295. AND IEEE Std 3004.8-2016. Recommended Practice for Generator Protection. Section: Synchronization and Paralleling. | https://search.abb.com/library/Download.aspx?DocumentID=9AKK108466A1295 | Detective Controls | How the FM can be detected. (optional)
SWB-08 | Load Sharing System | Load sharing failure | Generator control, governor or AVR faults cause uneven active or reactive load distribution. One generator may become overloaded while others remain lightly loaded. | Overloaded generators overheat and experience voltage or frequency instability. Protective trips may occur. | Reduced generating capacity and increased blackout risk can impact propulsion and essential services | 8 | 8 | Power management system monitoring; load trending; generator performance review; alarm monitoring | Routine load sharing tests; controller calibration; AVR maintenance; governor tuning | Electrical Engineer; Chief Engineer; Service Engineer | ABB. Motor and Generator Preventive Maintenance. Document No. 9AKK108466A1295. AND Woodward Generator Load Sharing and Control Systems Manual. | https://search.abb.com/library/Download.aspx?DocumentID=9AKK108466A1295 | Preventive Controls | How the FM can be prevented. (optional)
SWB-09 | Protection System | Blackout | Major bus faults, cascading generator trips, protection coordination failures or bus tie logic errors result in total loss of electrical supply. Redundancy is insufficient to sustain essential loads. | The switchboard becomes de-energised and all connected services lose power. Emergency systems and blackout recovery functions must operate correctly. | Loss of propulsion, navigation support systems, cargo operations, dynamic positioning and and essential services. This represents a critical vessel-level event. | 10 | 4 | PMS monitoring; generator status monitoring; event recorder analysis; blackout recovery testing | Redundancy management; protection coordination studies; crew drills; preventive maintenance of generation and distribution systems | Chief Engineer; Electrical Engineer | Schneider Electric. FlexSet Switchboards Instruction Bulletin. Document No. JYT1078000. Section: Maintaining the Switchboard. Periodic inspection, busbar maintenance, breaker testing and maintenance requirements. | https://productinfo.se.com/jyt1078000_flexset_switchboards_ib/ | Responsibility | Who is responsible for addressing the FM. (optional)