## Asset 23 - Gen Alarm & PA FM
Failure_ID | Category | Specific Failure Mode / Threat / Anomaly Name | Detailed Description & Technical Mechanism | Causes | Source | Link
GAPA-S01 | Sensor & Data Input Failures | Speaker-Line Impedance / Supervision Monitoring Fault | Networked PA/GA systems continuously supervise each speaker loop by impedance (and individual speaker monitoring). A monitoring fault reports a line as healthy while a speaker circuit is open or shorted, so a zone is silently dead and the fault is discovered only during an actual emergency. | Supervision-card/sensing fault, drift in impedance thresholds, or loss of the monitoring channel. | Sea Safety Marine - I-PAS Industrial Public Address & General Alarm System | https://seasafetymarine.com/product/i-pas-industrial-public-address-general-alarm-system/
GAPA-S02 | Sensor & Data Input Failures | Amplifier Self-Supervision / Fault-Detection Failure | Supervised amplifiers monitor themselves to trigger transfer to a hot-standby amplifier on failure. If fault detection fails, a dead amplifier is not detected and the standby is never engaged, leaving its lines without audio. | Amplifier supervision-circuit fault or mis-set fault thresholds. | TOA Electronics - Maritime PA/GA System (VX-3000) | https://www.toa.co.uk/solutions/maritime
GAPA-S03 | Sensor & Data Input Failures | Microphone Capsule / Call-Station Input Fault | Monitoring begins at the microphone capsule. A faulty capsule or call station yields no or garbled announcements; in decentralized systems a single call-station failure is required not to degrade overall performance, so an undetected fault here is a single-point-of-failure concern. | Capsule degradation, connector corrosion, or call-station electronics fault. | TOA Electronics - Maritime PA/GA System (VX-3000) | https://www.toa.co.uk/solutions/maritime
GAPA-N01 | Network & Communication Failures | Loss of GA/PA Network Backbone (IP/Fibre Systems) | Modern PA/GA systems are IP-networkable / fibre-ready with distributed access panels. Loss of the backbone isolates zones or cuts access panels off from the central controller, preventing announcements or alarm initiation from affected stations. | Network switch/fibre fault, cabling damage, or controller network-interface failure. | Solas Marine - PAGASYS Digital Public Address & General Alarm (networked) | https://solasmarine.com/product/pagasys-digital-public-address-and-general-alarm-systems-with-networked-options/
GAPA-N02 | Network & Communication Failures | GA/PA <-> Fire-Alarm Interface Fault | PA/GA integrates with fire detection so a confirmed fire can auto-trigger the alarm/evacuation message. An interface fault prevents a fire-initiated alarm from broadcasting, or produces spurious triggers. | Faulty dry-contact/serial interface to the fire-detection system or mis-configured I/O mapping. | TOA Electronics - Maritime PA/GA System (VX-3000) | https://www.toa.co.uk/solutions/maritime
GAPA-N03 | Network & Communication Failures | Loss / Corruption of Status Reporting to AMS | System health and fault/disable status sent to the AMS is lost or corrupted, hiding a degraded GA/PA (e.g., a failed amplifier or muted zone) from the watchkeeper. | Interface fault, fieldbus corruption, or controller comms-stack hang. | TAGSIA - Maritime OT Cybersecurity Glossary (IACS UR E26/E27, IEC 62443) | https://tagsia.com/intelligence/glossary/
GAPA-L01 | Control Logic & Software Failures | Priority / Override Logic Fault (Diode Matrix / DSP) | Priority logic ensures the general alarm overrides paging and entertainment and mutes local loudspeakers during emergency paging. A logic fault can let background music or paging block the general alarm, or fail to mute local speakers, degrading the emergency signal. | Diode-matrix/DSP priority configuration fault or software error. | Inameq - Public Address and General Alarm System for Marine | https://inameq.com/fire-fighting-system/public-address-general-system/
GAPA-L02 | Control Logic & Software Failures | Tone / Voice-Message Generation (DSP) Fault | On-board DSP generates the general-alarm tone (seven short blasts plus one long) and pre-recorded voice messages. A DSP fault yields an absent/incorrect tone or corrupted voice directions, undermining recognisable alerting. | DSP hardware/firmware fault or corrupted tone/message tables. | Solas Marine - PAGASYS Digital Public Address & General Alarm (networked) | https://solasmarine.com/product/pagasys-digital-public-address-and-general-alarm-systems-with-networked-options/
GAPA-L03 | Control Logic & Software Failures | Zone Selection / Routing Logic Fault | The system routes messages to selected zones (with at least one feeder per vertical fire zone). A routing fault sends the message to the wrong zones or fails to reach all required areas. | Zone-mapping configuration error or routing-logic fault. | US eCFR Title 46 Part 113 - Communication & Alarm Systems (Public Address) | https://www.ecfr.gov/current/title-46/chapter-I/subchapter-J/part-113/subpart-113.50
GAPA-L04 | Control Logic & Software Failures | GA/PA Stop-Signal Handshake Logic Fault | Dry-contact P/A-STOP and E.G/A-STOP handshakes coordinate the general-alarm and PA equipment. A logic fault can leave the PA muted when it should broadcast, or fail to stop entertainment during an alarm. | Faulty stop-signal contact wiring or handshake-logic error. | Inameq - Public Address and General Alarm System for Marine | https://inameq.com/fire-fighting-system/public-address-general-system/
GAPA-A01 | Actuator & Switching Failures | Hot-Standby Amplifier Transfer Failure | The hot-standby module should transfer the speaker load to a standby amplifier when the primary fails. Failure of the transfer relay/module leaves the affected lines silent despite a healthy standby being present. | Transfer-relay/module failure or control-signal fault. | Sea Safety Marine - I-PAS Industrial Public Address & General Alarm System | https://seasafetymarine.com/product/i-pas-industrial-public-address-general-alarm-system/
GAPA-A02 | Actuator & Switching Failures | General-Alarm Contact-Maker / Initiating Switch Failure | The bridge general-emergency-alarm contact maker initiates the GA. A stuck/no-make contact prevents initiation of the alarm, while a short produces a spurious general alarm. | Contact-maker mechanical failure, wiring fault, or short circuit. | Inameq - Public Address and General Alarm System for Marine | https://inameq.com/fire-fighting-system/public-address-general-system/
GAPA-A03 | Actuator & Switching Failures | Power Auto-Changeover (AC -> 24 V DC) Failure | The system should switch automatically from 110/220 V AC to its 24 V DC battery supply on mains loss. Changeover failure loses the entire PA/GA when main power is lost - precisely when alerting may be needed. | Changeover-relay fault, depleted or faulty battery, or charger failure. | Inameq - Public Address and General Alarm System for Marine | https://inameq.com/fire-fighting-system/public-address-general-system/
GAPA-P01 | Process & Functional Failures | Loudspeaker Failure / Inaudibility in a Space | A loudspeaker can fail or become inaudible from burnout, water ingress and corrosion (decks) or high background noise and heat (engine rooms). As loudspeakers must not have local cut-outs, a silent space indicates a hardware/cabling failure that defeats audibility with doors closed. | Speaker burnout, enclosure ingress/corrosion, cable fault, or insufficient SPL versus background noise. | Marine PA/GA Speaker Specifications (open decks & engine rooms) | https://www.karinadispatch.com/2026/05/marine-paga-speaker-specifications-what.html
GAPA-P02 | Process & Functional Failures | Amplifier Failure -> Loss of Audio Output | Failure of an amplifier without a successful standby transfer silences all connected speaker lines. Regulation requires the amplifier (and GA signal device) to be provided in duplicate for this reason. | Amplifier component failure combined with failed/absent redundancy. | US eCFR Title 46 Part 113 - Communication & Alarm Systems (Public Address) | https://www.ecfr.gov/current/title-46/chapter-I/subchapter-J/part-113/subpart-113.50
GAPA-P03 | Process & Functional Failures | Feedback / Distortion Degrading Intelligibility | Acoustic feedback or distortion reduces speech intelligibility below a usable level, so announcements are heard but not understood. Loudspeakers must be located to eliminate feedback for this reason. | Poor speaker placement, excessive gain, or amplifier distortion. | US eCFR Title 46 Part 113 - Communication & Alarm Systems (Public Address) | https://www.ecfr.gov/current/title-46/chapter-I/subchapter-J/part-113/subpart-113.50
GAPA-P04 | Process & Functional Failures | Zone Feeder / Branch-Cable Loss | Damage, fire or a fault on a zone feeder or branch circuit disables a zone. Feeders and branch cables are required to run in passageways with one feeder per fire zone to limit this exposure. | Cable damage, fire, connector failure, or distribution-panel fault. | US eCFR Title 46 Part 113 - Communication & Alarm Systems (Public Address) | https://www.ecfr.gov/current/title-46/chapter-I/subchapter-J/part-113/subpart-113.50
GAPA-H01 | Hardware & Equipment Failures | Central Control Unit / Power-Supply Module Failure | Failure of the main control unit or a power-supply module can disable the system unless duplicated; modular designs mitigate with hot-swappable amplifiers and power supplies. | Main-unit electronics failure or PSU failure without redundancy. | Sea Safety Marine - I-PAS Industrial Public Address & General Alarm System | https://seasafetymarine.com/product/i-pas-industrial-public-address-general-alarm-system/
GAPA-H02 | Hardware & Equipment Failures | Enclosure Water Ingress / Corrosion (Weather Locations) | Loss of watertight integrity (IP56 / NEMA Type 4-4X) on weather-deck subsystems lets moisture/salt cause electrical failure of speakers, beacons or junction boxes. | Seal degradation, corrosion, or mechanical damage to weather-rated enclosures. | US eCFR Title 46 Part 113 - Communication & Alarm Systems (Public Address) | https://www.ecfr.gov/current/title-46/chapter-I/subchapter-J/part-113/subpart-113.50
GAPA-C01 | Cyberthreats | Unauthorized Activation / Spoofed General Alarm | The PA is required to be protected against unauthorized use. An attacker with system access can trigger a false general alarm or hijack the PA to broadcast false instructions, causing panic and eroding trust in alerts, or mask a genuine event. | Weak/absent access control on call stations, network or configuration interfaces. | US eCFR Title 46 Part 113 - Communication & Alarm Systems (Public Address) | https://www.ecfr.gov/current/title-46/chapter-I/subchapter-J/part-113/subpart-113.50
GAPA-C02 | Cyberthreats | Alarm Suppression via Networked-Controller Manipulation | On IP-networked PA/GA, an adversary suppresses the general-alarm broadcast or its fault alarms (or disables hot-standby transfer) while the HMI shows normal status, so a real emergency alarm never sounds in the affected zones. | Unauthenticated control-network access and manipulation of CBS/controller state (IACS UR E26/E27 scope). | CYDOME - Maritime Cybersecurity Bulletin (Nov 2025): PLC/HMI CVEs | https://cydome.io/maritime-cybersecurity-bulletin-november-7-2025/
GAPA-C03 | Cyberthreats | Pre-Recorded Message / DSP Tampering | Modification of stored voice messages or tone tables (via the configuration port or network) causes the system to broadcast incorrect emergency instructions while appearing to operate normally. | Unprotected configuration upload (e.g., USB/network) or compromised engineering access. | TAGSIA - Maritime OT Cybersecurity Glossary (IACS UR E26/E27, IEC 62443) | https://tagsia.com/intelligence/glossary/