## Asset 30 - Aux Boiler FM
Failure_ID | Category | Specific Failure Mode / Threat / Anomaly Name | Detailed Description & Technical Mechanism | Causes | Source | Link
AUXB-S01 | Sensor & Data Input Failures | Water-Level Sensor / Gauge Misreading | Drum level governs feed control and the low/high-level trips. A false level lets the controller overfeed (priming, carryover, water hammer) or underfeed, risking low-water dry-firing and tube overheating. | Level transmitter fault, fouled/blocked sensing connections, or gauge-glass error. | ShipFever - Boiler Alarms and Trips | https://shipfever.com/boiler-alarms-and-trips/
AUXB-S02 | Sensor & Data Input Failures | Steam-Pressure Transmitter Fault | A drifting/failed pressure transmitter causes the combustion control to under-fire (loss of steam) or over-fire toward over-pressure and safety-valve lift. | Transmitter drift, blocked impulse line, or electrical fault. | ShipFever - Boiler Alarms and Trips | https://shipfever.com/boiler-alarms-and-trips/
AUXB-S03 | Sensor & Data Input Failures | Drum-Level Swell/Shrink Misinterpretation | Rapid load changes cause transient swell/shrink; if the controller does not compensate, it may trip on false high/low level or take incorrect feed action. | Single-element control under transient load, or poor controller tuning. | ShipFever - Boiler Alarms and Trips | https://shipfever.com/boiler-alarms-and-trips/
AUXB-N01 | Network & Communication Failures | Loss of Status / Telemetry to AMS | Boiler level, pressure, alarms and trip status are reported to the AMS. Loss of the link removes remote awareness of an excursion (e.g., low water) during unattended/UMS periods. | Cable/connector fault, fieldbus master failure, or controller comms hang. | TAGSIA - Maritime OT Cybersecurity Glossary (IACS UR E26/E27, IEC 62443) | https://tagsia.com/intelligence/glossary/
AUXB-N02 | Network & Communication Failures | Fieldbus Corruption / Spoofed Boiler Status | Corrupted or forged status frames can suppress a low-water or over-pressure alarm at the AMS or assert false-safe values, breaking the link between displayed and physical state. | Unauthenticated legacy fieldbus, electrical noise, or bus contention. | Enhancing Maritime Cybersecurity through OT Sensor Data Fusion (Sensors, 2024) | https://www.ncbi.nlm.nih.gov/pmc/articles/PMC11174856/
AUXB-L01 | Control Logic & Software Failures | Automatic Combustion Control Failure | The boiler fails to fire/modulate on automatic and must be reverted to manual firing; in manual mode many alarms and cut-outs may be inactive, reducing protection. | Combustion-control unit fault, sensor input fault, or controller failure. | Marine Inbox - Troubleshootings for Auxiliary Boiler | https://marineinbox.com/marine-exams/troubleshootings-for-auxiliary-boiler/
AUXB-L02 | Control Logic & Software Failures | Feedwater Control Logic Fault | Errors in feed-pump start/stop or feed-valve modulation drive the drum toward low or high level excursions. | Control logic error, feed-valve positioner fault, or level-input fault. | ShipFever - Boiler Alarms and Trips | https://shipfever.com/boiler-alarms-and-trips/
AUXB-L03 | Control Logic & Software Failures | Safety Interlock / Sequence Logic Failure or Bypass | Purge, ignition, level and pressure interlocks enforce safe start-up and operation. Logic failure or bypass (e.g., to keep the boiler running) removes protection against over-pressure, low water and furnace explosion. | Software fault, defeated interlock, or operation in manual with reduced safeties. | Chief Engineer Log - Marine Oil-Fired Boiler Operation | https://chiefengineerlog.com/2022/03/30/what-is-marine-oil-fired-boiler-and-how-to-correctly-operate-it/
AUXB-A01 | Actuator & Mechanical Control Failures | Feed-Water Regulating Valve / Feed Pump Failure | A stuck feed valve or tripped feed pump produces low level (overheating risk) or high level (carryover), depending on failure direction. | Valve/positioner seizure, pump trip, or loss of feed-water supply. | ShipFever - Boiler Alarms and Trips | https://shipfever.com/boiler-alarms-and-trips/
AUXB-A02 | Actuator & Mechanical Control Failures | Safety Valve Malfunction | A safety valve stuck shut removes over-pressure protection; lifting early or passing causes steam loss and pressure-control instability. | Spring fatigue, corrosion/scaling on the seat, or incorrect set pressure. | ShipFever - Boiler Alarms and Trips | https://shipfever.com/boiler-alarms-and-trips/
AUXB-A03 | Actuator & Mechanical Control Failures | Main Steam Stop / Blowdown Valve Failure | Passing or seized steam-stop/blowdown valves cause uncontrolled steam loss, inability to isolate, or loss of water-chemistry control. | Seat wear, corrosion, or actuator fault. | Chief Engineer Log - Marine Oil-Fired Boiler Operation | https://chiefengineerlog.com/2022/03/30/what-is-marine-oil-fired-boiler-and-how-to-correctly-operate-it/
AUXB-P01 | Process & Mechanical Failures | Low Water Level -> Tube Overheating / Dry Firing | Loss of feed with a failed low-level trip exposes heating surfaces above the water line; tubes overheat and can rupture, with serious safety consequences. | Feed failure combined with failed/blocked low-water protection. | ShipFever - Boiler Alarms and Trips | https://shipfever.com/boiler-alarms-and-trips/
AUXB-P02 | Process & Mechanical Failures | Water Carryover / Priming | High level or poor water chemistry carries water with the steam, causing water hammer and contamination of steam-using services. | High drum level, high TDS/foaming, or rapid load swing. | ShipFever - Boiler Alarms and Trips | https://shipfever.com/boiler-alarms-and-trips/
AUXB-P03 | Process & Mechanical Failures | Gas-Side Soot / Water-Side Scale Fouling | Fouling reduces heat transfer, lowering steam output and raising fuel consumption and exhaust temperature; heavy soot also raises smoke density and uptake-fire risk. | Incomplete combustion/soot deposition or poor feed-water treatment (scale). | Marine Inbox - Troubleshootings for Auxiliary Boiler | https://marineinbox.com/marine-exams/troubleshootings-for-auxiliary-boiler/
AUXB-P04 | Process & Mechanical Failures | Boiler Implosion (Vacuum Collapse) | Cooling a closed boiler without venting creates internal vacuum that can collapse pressure parts; vents are provided specifically to prevent this. | Shutting/cooling the boiler without opening air vents. | ShipFever - Boiler Alarms and Trips | https://shipfever.com/boiler-alarms-and-trips/
AUXB-H01 | Hardware & Equipment Failures | Boiler Tube / Pressure-Part Rupture | Structural failure of tubes or pressure parts releases steam/water and forces shutdown. | Corrosion, thermal fatigue, scale-induced overheating, or material defect. | Chief Engineer Log - Marine Oil-Fired Boiler Operation | https://chiefengineerlog.com/2022/03/30/what-is-marine-oil-fired-boiler-and-how-to-correctly-operate-it/
AUXB-H02 | Hardware & Equipment Failures | Refractory / Furnace Lining Failure | Cracked or collapsed refractory exposes structure to flame, distorts heat distribution and can damage the furnace. | Thermal cycling, water/oil ingress, or ageing of refractory. | Chief Engineer Log - Marine Oil-Fired Boiler Operation | https://chiefengineerlog.com/2022/03/30/what-is-marine-oil-fired-boiler-and-how-to-correctly-operate-it/
AUXB-C01 | Cyberthreats | Falsified Level / Pressure Telemetry (Defeat Safety Trips) | An attacker injects safe-looking level/pressure values to the controller/AMS while a dangerous low-water or over-pressure condition develops, suppressing alarms and defeating protective trips - a high-consequence safety attack. | Manipulation of unauthenticated OT sensor/HMI data on machinery networks. | Enhancing Maritime Cybersecurity through OT Sensor Data Fusion (Sensors, 2024) | https://www.ncbi.nlm.nih.gov/pmc/articles/PMC11174856/
AUXB-C02 | Cyberthreats | Boiler PLC / Control Logic Manipulation | Unauthorized modification of boiler PLC/control logic alters interlocks, set-points or trip thresholds while the HMI shows normal status; marine HMI/PLC configuration software has documented exploitable vulnerabilities. | Category III PLCs without authentication; exploitable engineering/HMI software (known CVEs). | CYDOME - Maritime Cybersecurity Bulletin (Nov 2025): PLC/HMI CVEs | https://cydome.io/maritime-cybersecurity-bulletin-november-7-2025/