## Asset 31 - Boiler Burner FM
Failure_ID | Category | Specific Failure Mode / Threat / Anomaly Name | Detailed Description & Technical Mechanism | Causes | Source | Link
BURN-S01 | Sensor & Data Input Failures | Flame Scanner / Flame-Eye Failure or Fouling | The flame detector confirms combustion. A dirty/failed scanner causes nuisance flame-failure trips; far more dangerously, a false flame-present signal keeps the fuel valve open with no flame, letting fuel accumulate in the furnace - a primary furnace-explosion mechanism. | Soot fouling of the photocell/scanner lens, detector ageing/failure, or wiring fault. | ShipFever - How to Perform Boiler Flame Failure Test | https://shipfever.com/boiler-flame-failure-test/
BURN-S02 | Sensor & Data Input Failures | Burner FO Pressure / Temperature Transmitter Fault | Atomisation needs fuel within a set pressure band (typically ~2-4 bar) and correct viscosity. A faulty pressure/temperature signal disturbs the air-fuel ratio, causes low-FO-pressure trips, or yields poor atomisation. | Transmitter drift, blocked sensing line, dirty burner fine-filter/dirt-trap, or heater fault. | Marine Insight - Flame Failure / Fuel Pump Tripping in Aux Boilers | https://www.marineinsight.com/tech/boiler/what-to-do-when-flame-failure-or-fuel-pump-tripping-in-marine-auxiliary-boilers-occurs/
BURN-N01 | Network & Communication Failures | Loss of Burner Status to AMS | Burner sequence and trip status are reported to the AMS. Loss of the link hides flame-failure, lockout or trip conditions from the watchkeeper. | Cable/connector fault, fieldbus master failure, or controller comms hang. | TAGSIA - Maritime OT Cybersecurity Glossary (IACS UR E26/E27, IEC 62443) | https://tagsia.com/intelligence/glossary/
BURN-N02 | Network & Communication Failures | Spoofed / Corrupted Burner Sequence Status | Corrupted or forged frames mask a lockout/flame-failure indication or assert false-normal status, hiding an unsafe combustion condition. | Unauthenticated legacy fieldbus, electrical noise, or bus contention. | Enhancing Maritime Cybersecurity through OT Sensor Data Fusion (Sensors, 2024) | https://www.ncbi.nlm.nih.gov/pmc/articles/PMC11174856/
BURN-L01 | Control Logic & Software Failures | Burner Management Sequence Controller Fault | The burner management system (BMS) sequences purge, ignition, fuel admission and modulation. A sequencing fault can mistime fuel admission relative to ignition/purge, causing failed light-off or unsafe fuel admission. | BMS logic error, timer fault, or feedback (limit-switch/position) mismatch. | Marine Insight - Boiler Starting Failure Troubleshooting | https://www.marineinsight.com/tech/boiler/boiler-starting-failure-troubleshooting/
BURN-L02 | Control Logic & Software Failures | Inadequate Pre-Purge Logic Failure | Pre-purge clears unburnt fuel/vapour before ignition. Skipped or shortened purge allows accumulation that ignites violently - a leading cause of furnace explosions. | Purge-timer fault, defeated purge interlock, or air-flow proving fault. | ShipFever - How to Perform Boiler Flame Failure Test | https://shipfever.com/boiler-flame-failure-test/
BURN-L03 | Control Logic & Software Failures | Flame-Failure Response / Supervision Misconfiguration | An over-long flame-failure response time, or flame-supervision wrongly disabled outside the start sequence, delays fuel cut-off after flame loss, allowing fuel to enter an unlit furnace. | Incorrect response-time setting, supervision override left active, or detector self-check disabled. | ShipFever - Boiler Alarms and Trips | https://shipfever.com/boiler-alarms-and-trips/
BURN-A01 | Actuator & Mechanical Control Failures | Fuel Solenoid / Quick-Closing Valve Failure | Failure to close on a trip leaves fuel flowing to an unlit furnace (explosion hazard); failure to open prevents firing. | Solenoid coil failure, valve seat fouling, or actuator/air-supply fault. | ShipFever - How to Perform Boiler Flame Failure Test | https://shipfever.com/boiler-flame-failure-test/
BURN-A02 | Actuator & Mechanical Control Failures | Ignition Transformer / Electrode Failure | No spark across the electrodes prevents ignition and trips the boiler on flame failure; weak/intermittent spark causes unreliable light-off. | Ignition transformer failure, electrode fouling/gap maladjustment, or HT lead fault. | Marine Inbox - Troubleshootings for Auxiliary Boiler | https://marineinbox.com/marine-exams/troubleshootings-for-auxiliary-boiler/
BURN-A03 | Actuator & Mechanical Control Failures | Combustion-Air Damper / FD Fan Actuator Failure | Incorrect air delivery causes low-airflow trips or rich/lean combustion; loss of proving air aborts light-off. | Damper actuator/linkage fault, FD fan trip, or air-proving switch fault. | ShipFever - How to Perform Boiler Flame Failure Test | https://shipfever.com/boiler-flame-failure-test/
BURN-A04 | Actuator & Mechanical Control Failures | Burner Not in Firing Position | If the burner fails to reach its firing position, the sequence trips to prevent fuel admission without a stable spark/flame path. | Burner-positioning motor fault, limit-switch fault, or mechanical obstruction. | ShipFever - Boiler Alarms and Trips | https://shipfever.com/boiler-alarms-and-trips/
BURN-P01 | Process & Mechanical Failures | Atomiser / Nozzle Clogging | A clogged main atomiser or pilot-burner nozzle prevents proper fuel atomisation, causing flame failure or unstable combustion. | Sludge/carbon deposits in the nozzle, dirty fuel, or poor upstream filtration. | Marine Insight - Boiler Starting Failure Troubleshooting | https://www.marineinsight.com/tech/boiler/boiler-starting-failure-troubleshooting/
BURN-P02 | Process & Mechanical Failures | Poor Atomisation / Incomplete Combustion | Wrong fuel temperature/pressure or air-fuel ratio produces soot, smoke and carbon deposits, raising smoke density (and potential port-state intervention) and fouling heat surfaces. | Off-design FO viscosity/pressure, worn atomiser, or maladjusted air-fuel ratio. | Marine Inbox - Troubleshootings for Auxiliary Boiler | https://marineinbox.com/marine-exams/troubleshootings-for-auxiliary-boiler/
BURN-P03 | Process & Mechanical Failures | Flashback / Flame Instability | On rotary-cup/gas burners the flame can retreat to the burner plate at low firing, damaging burner components such as electrode covers and cabling. | Incorrect atomising air/steam pressure, low firing-rate instability, or fuel-changeover error. | Marine Insight - Boiler Starting Failure Troubleshooting | https://www.marineinsight.com/tech/boiler/boiler-starting-failure-troubleshooting/
BURN-H01 | Hardware & Equipment Failures | Burner Fan Motor / Bearing Failure | Failure of the combustion-air fan stops air delivery and aborts/forbids firing. | Motor winding/bearing failure or loss of electrical supply. | Marine Insight - Flame Failure / Fuel Pump Tripping in Aux Boilers | https://www.marineinsight.com/tech/boiler/what-to-do-when-flame-failure-or-fuel-pump-tripping-in-marine-auxiliary-boilers-occurs/
BURN-H02 | Hardware & Equipment Failures | Burner Fuel Pump Failure / Tripping | Fuel-pump failure or repeated tripping on low pressure prevents stable firing. | Pump mechanical failure, low-suction/pressure trip, or upstream supply fault. | Marine Insight - Flame Failure / Fuel Pump Tripping in Aux Boilers | https://www.marineinsight.com/tech/boiler/what-to-do-when-flame-failure-or-fuel-pump-tripping-in-marine-auxiliary-boilers-occurs/
BURN-C01 | Cyberthreats | Flame-Scanner Signal Spoofing (Defeat Flame-Failure Device) | Injecting a false flame-present signal keeps the fuel valve open with no flame, driving fuel accumulation toward furnace explosion; injecting false flame-failure forces repeated nuisance trips (denial of steam). This targets the burner's most safety-critical sensor. | Manipulation of unauthenticated OT sensor signals/HMI on the machinery network. | Enhancing Maritime Cybersecurity through OT Sensor Data Fusion (Sensors, 2024) | https://www.ncbi.nlm.nih.gov/pmc/articles/PMC11174856/
BURN-C02 | Cyberthreats | BMS PLC Logic / Firmware Manipulation (Purge/Interlock Disable) | Unauthorized change to burner-management PLC logic disables pre-purge or the flame-failure trip while the HMI shows normal sequencing, creating a furnace-explosion pathway; marine PLC/HMI software has documented exploitable vulnerabilities. | Category III PLCs without authentication; exploitable HMI/engineering software (known CVEs). | CYDOME - Maritime Cybersecurity Bulletin (Nov 2025): PLC/HMI CVEs | https://cydome.io/maritime-cybersecurity-bulletin-november-7-2025/